MATHEMATICS AND COMPUTATIONS BASIS

1. BASE VALUES & CONSTANTS

basekV = 13.7;        // System base voltage (13.7 kV)

Sbase = 25000;         // 25 kVA base per transformer

transformerPF = 0.9;   // Transformer rated power factor

BFS_TOLERANCE = 0.0001; // Convergence tolerance

BFS_MAX_ITER = 50;     // Maximum iterations

2. IMPEDANCE CALCULATIONS (Z = R + jX)

Line Impedance Data (from staking sheet):

// DISTRIBUTED SYSTEM

meter1: { r: 0.0114, x: 0.0473 }  // Z₁ = 0.0114 + j0.0473 Ω

meter2: { r: 0.0055, x: 0.0226 }  // Z₂ = 0.0055 + j0.0226 Ω

meter3: { r: 0.0011, x: 0.0046 }  // Z₃ = 0.0011 + j0.0046 Ω

// CENTRALIZED SYSTEM

main: { r: 0.0158, x: 0.0656 }    // Zc = 0.0158 + j0.0656 Ω

Impedance Magnitude:

text

|Z| = √(R² + X²)

|Z₁| = √(0.0114² + 0.0473²) = 0.0487 Ω (HIGH)

|Z₂| = √(0.0055² + 0.0226²) = 0.0233 Ω (MEDIUM)

|Z₃| = √(0.0011² + 0.0046²) = 0.0047 Ω (LOW)

|Zc| = √(0.0158² + 0.0656²) = 0.0675 Ω (CENTRALIZED)

Meter 1 (HIGH Z): Longest feeder, smaller conductor

Meter 2 (MED Z): Medium distance

Meter 3 (LOW Z): Shortest feeder, largest conductor

Centralized: Single long feeder to all 12 buses

3. LOAD MULTIPLIER (POWER SCALING)

Base Power Calculation:

javascript

// Base active power (kW)

Pbase[i] = bus.kva × transformerPF

// Base reactive power (kVAR)

Qbase[i] = bus.kva × √(1 - transformerPF²)

// Examples:

M1-A1 (50 kVA): P = 50 × 0.9 = 45 kW, Q = 50 × √(1-0.81) = 21.8 kVAR

M2-B1 (100 kVA): P = 90 kW, Q = 43.6 kVAR

Actual Power with Load Multiplier:

P = Pbase × LM × meterFactor

Q = Qbase × LM × meterFactor × (PF / 0.95)

// Where:

// LM = Global Load Multiplier (0.5 to 2.0)

// meterFactor = Per-meter multiplier (0.5 to 2.0)

// PF = Power Factor setting (0.5 to 1.0)

// Example: LM=1.5, meterFactor=1.0, PF=0.95

P = 45 × 1.5 × 1.0 = 67.5 kW

Q = 21.8 × 1.5 × 1.0 × (0.95/0.95) = 32.7 kVAR

Apparent Power:

S = √(P² + Q²)  // in kVA

Example: S = √(67.5² + 32.7²) = 75 kVA

4. IMPEDANCE MULTIPLIER (Z SCALING)

// Final impedance after multiplier

R_final = R_base × Z_mult

X_final = X_base × Z_mult

// Where Z_mult = Impedance Multiplier (0.5 to 3.0)

// Example: Z_mult = 2.0 for Meter 1

R = 0.0114 × 2.0 = 0.0228 Ω

X = 0.0473 × 2.0 = 0.0946 Ω

|Z| = √(0.0228² + 0.0946²) = 0.0974 Ω (DOUBLED!)

5. CURRENT CALCULATION (I)

// Current magnitude in per unit

I = S / V  // where S in MVA, V in pu

// Convert to Amperes

I_amps = I × Sbase / (√3 × Vbase)

// Example: S = 75 kVA, V = 0.936 pu

I_pu = 0.075 / 0.936 = 0.0801 pu

I_amps = 0.0801 × 25000 / (1.732 × 230) = 5.03 A

6. VOLTAGE DROP CALCULATION

Basic Voltage Drop Formula:

ΔV = I × Z  (in per unit)

// Where:

// I = current in pu

// Z = impedance magnitude in pu

// Actual voltage:

V_child = V_parent – ΔV

With Scaling Factors:

// For DISTRIBUTED system

dropScale = 3.5

ΔV = I × Z × dropScale

V_child = Math.max(0.70, V_parent - ΔV)

// For CENTRALIZED system

dropScale = 0.35

ΔV = I × Z × dropScale

V_child = V_parent - ΔV  // No lower bound during calculation

Distributed: Shorter feeders, less cumulative drop

Centralized: Long feeder, need smaller scale to prevent collapse

7. POWER FACTOR EFFECT

// Reactive power adjustment with PF

Q = P × tan(acos(PF))

// Current magnitude increases as PF decreases

I = √(P² + Q²) / V

// Example: P = 45 kW, PF = 0.8

Q = 45 × tan(acos(0.8)) = 45 × 0.75 = 33.75 kVAR

S = √(45² + 33.75²) = 56.25 kVA

I = 56.25 / (0.936 × 1000) = 0.0601 pu (20% higher than at PF=0.95!)

8. LOSS CALCULATIONS

Copper Losses (I²R):

P_loss = I² × R × 1000  // in Watts

// Example: I = 0.0801 pu, R = 0.0114 Ω

P_loss = (0.0801)² × 0.0114 × 1000 = 0.073 kW = 73 W

Core Losses (Constant):

coreLoss = totalCapacity × 0.005  // 0.5% of rated kVA

// Distributed: 750 kVA × 0.005 = 3.75 kW

// Centralized: 1500 kVA × 0.005 = 7.5 kW

Harmonic Losses (THD Effect):

harmonicMultiplier = 1 + (THD / 100) × 2

harmonicLoss = totalCopperLoss × (harmonicMultiplier - 1) + (totalLoad × 0.005 × (THD / 5))

// Example: THD = 10%, totalCopperLoss = 1.98 kW, totalLoad = 675 kW

harmonicMultiplier = 1 + 0.1 × 2 = 1.2

harmonicLoss = 1.98 × (1.2 - 1) + (675 × 0.005 × 2) = 0.396 + 6.75 = 7.15 kW

Total Losses:

P_total_loss = P_copper + P_core + P_harmonic

Example: 1.98 + 3.75 + 7.15 = 12.88 kW

Loss % = (12.88 / 675) × 100 = 1.91%

9. PEC STANDARD (Philippine Electrical Code)

Voltage Drop Limits:

Maximum Allowable Drop = 5% of nominal voltage

V_minimum = 1.0 - 0.05 = 0.95 pu

Status Classification:

- GOOD: V ≥ 0.97 pu (≤3% drop)

- WARNING: 0.95 ≤ V < 0.97 pu (3-5% drop)

- VIOLATION: V < 0.95 pu (>5% drop)

PEC Compliance Check:

isCompliant = worstV ≥ 0.95

// From results:

M1-A6 = 0.9361 pu →  VIOLATION (6.39% drop)

M2-B3 = 0.9664 pu →  WARNING (3.36% drop)

M3-C3 = 0.9967 pu →  GOOD (0.33% drop)

10. BACKWARD-FORWARD SWEEP ALGORITHM

Step 1: Initialize

V[source] = 1.0 pu

V[others] = 1.0 pu (initial guess)

I[branches] = 0

Step 2: Calculate Load Currents

I_load[i] = S_i / V[i]  // for each load bus

Step 3: Backward Sweep (Sum currents)

I_branch[j] = I_load[to_node] + Σ(I_children)

Step 4: Forward Sweep (Calculate voltages)

V[child] = V[parent] - I_branch × Z

Step 5: Check Convergence

maxDeviation = max(|V_new - V_old|)

if maxDeviation < tolerance: converged

else: repeat steps 2-5

11. DISTRIBUTED vs CENTRALIZED COMPARISON

Distributed System:

Each meter independent:

V_m1 = 1.0 - I₁ × Z₁ × 3.5

V_m2 = 1.0 - I₂ × Z₂ × 3.5

V_m3 = 1.0 - I₃ × Z₃ × 3.5

Result: 0.9967 (M3) > 0.9664 (M2) > 0.9361 (M1)

Centralized System:

Cumulative drops:

V_bus1 = 1.0 - I × Z1 × 0.35

V_bus2 = V_bus1 - I × Z2 × 0.35

...

V_bus12 = V_bus11 - I × Z12 × 0.35

Result: 0.9943 > 0.9405 > 0.8877

12. ALL FORMULAS

| Quantity | Formula | Units |
| --- | --- | --- |
| Impedance | Z = √(R² + X²) | Ω |
| Active Power | P = Pbase × LM × meterFactor | kW |
| Reactive Power | Q = P × tan(acos(PF)) | kVAR |
| Apparent Power | S = √(P² + Q²) | kVA |
| Current | I = S / V | pu |
| Voltage Drop | ΔV = I × Z × scale | pu |
| Copper Loss | P_loss = I² × R × 1000 | W |
| Core Loss | P_core = 0.005 × kVA_rated | kW |
| Harmonic Loss | P_harm = f(THD, P_copper, P_load) | kW |
| PEC Limit | V ≥ 0.95 pu | - |